The 2009 International Conference of Mechanical Engineering

London, U.K., 1-3 July, 2009

Special Tutorial

Safety Reliability Method Applied to Evaluate Smoke Control System of Fire Accident in the Tunnel of Mass Rapid Transit System

Ying-Che Weng, Tutorial Organizer

Ph.D. Candidate

Department of Mechanical Engineering, National Taiwan University

No.1, Sec. 4, Roosevelt Road, Taipei, Taiwan

Tel: 886-2-23631808

Fax: 886-2-23631755

E-mail: d95522029@ntu.edu.tw

Ming-Tsun Ke, Tutorial Chair

Associate professor

Department of Energy and Refrigerating Air-Conditioning Engineering National Taipei University of Technology

No.1, Sec. 3, Chung-hsiao E. Rd., Taipei, Taiwan

Tel: 886-2-27712171 ext.3509

Fax: 886-2-27314919

E-Mail: mtke@ntut.edu.tw

Sih-Li Chen, Tutorial Co-Chair

Professor

Department of Mechanical Engineering, National Taiwan University

No.1, Sec. 4, Roosevelt Road, Taipei, Taiwan

Tel: 886-2-23631808

Fax: 886-2-23631755

E-mail: slchen01@ntu.edu.tw

Tutorial Topic

We utilized CFD software to investigate smoke control system of safety reliability for the underground Mass Rapid Transit (MRT) system.

Session Goal

The purpose of this research is to simulate the fire occurring in the tunnel region where the smoke control system designs are corresponding to the National Federation of Paralegal Associations 130 (NFPA130).

Session Results

The smoke control mode of the tunnel includes the Tunnel Ventilation Fan (TVF) and Jet Air Fan (JAF) in the station. The control strategies of the TVF, the JAF, and the flow phenomenon of the smoke in the fire environment are simulated by commercial software, PHOENICS. In the numerical simulation, the results show that under the condition of turning on the TVF and JAF in 3 minutes later, if the fire in the tunnel region attains the criterion of temperature field (<60℃), the concentration of carbon monoxide (<1500ppm), radiation intensity (<6.3kW/m2) and visibility (10m), passengers can evacuate from these safe passages. The study presents reasonably good agreement with simulation data for the standard of NFPA130.